## Slide 1: Using KEPserverEx on Sierra Instruments Modbus products

## Slide 2: Setting up a MODBUS network using KEPserverEx OPC server to read data from a 620S/640S/780S
What you’ll need
  A PC with Kepserver EX 4.0
  A 2 wire RS485 interface on the PC. (RS232 to RS485, USB to RS485, or a PCI card)
  Twisted pair shielded cable
  A 620S/640S/780S with a MODBUS board
  Get a copies of the 600/700 Series Modbus Quick Install Guide, and 600/700 Series Modbus Instruction Manuals.
Determine what Baud rate, Parity , Slave node address you will be using.
  Sierra default is 19.2K baud, Even Parity, ID# 1 Node address
  This setting can be changed using the boot loader on our meter

## Slide 3
Install the KEPserverEx 4.0 software on your PC
Install the RS485 hardware and drivers on the PC
Make sure your PC has Microsoft HyperTerminal software
  Windows XP and Vista included HyperTerminal, you ‘ll need to add it to Win 7&8
  Other terminal programs can be used, but they must have XMODEM to update firmware
Connect wires between the 600/700 meter and the RS485 as shown in Chapter 1 of the 600/700 instruction manual
Change the 600/700 meter setting using HyperTerminal to whatever ID number (node address), Baud rate, Parity, Response Delay, Tag Name, FB byte order (normally 34,12) you decided to use. See Chapter 2
  Starting the Boot loader may take some practice. From the time you power your meter until you press Enter on the PC is about 2 seconds.

## Slide 4: Using the Boot loader to change the COM settings
Start HyperTerminal. Click Cancel, we’ll just edit the current connection.

## Slide 5: On the File menu, select Properties, then select the COM port you will be using. (COM1 here)

## Slide 6: Change the Bits per second (Baud) to 9600 Change the Flow Control to None.

## Slide 7: Here is the tricky part! Power up the meter, then press Enter within 2 seconds. If you miss the 2 second window, power down the meter and try again. If you succeed you will see the screen below.

## Slide 8: Press 2) to Setup up the Modbus board. C to change, N to look at the next entry. (ID changed from 255 to 1) Baud rate and Parity must match your Master’s settings.

## Slide 9: Press 3) to quit, or you’ll have to cycle the power on the meter. Press File>Exit or the X to close the window Click Yes on the dialog box to close HyperTerminal

## Slide 10: Using KepserverEx
KEPserverEx can be downloaded from http://www.kepware.com/
You can download a Demo Version for free
The current version of KEPsereverEx is 5.14. To reset the 2 hour demo timer you must restart your whole PC.
However I prefer the old KEPserverEx 4.0 because to reset the 2 hour demo timer you just restart the KEPserverEx program.
Install KEPserverEx on your PC

## Slide 11: Start KEPserverEx. For a fresh start click on File>New Click on Click to add a channel to add your master

## Slide 12: The easy way
Kepserver allow you to save setups in a file they named with a .opf
If someone had already written and saved one, you can use it by going to File>Open and browsing to fine the .opf file.

## Slide 13
Chances are you will be using a different COM port, so change it in the channel properties.

## Slide 14
All the other setting and tags will have been stored in the .opf file.
Click on the Hammer Icon to start the quick client
All the Data and tags configured by the .opf author will be visible.

## Slide 15: Doing your Own Type a name for your Channel name:

## Slide 16: Chose the Device driver, Modbus Serial

## Slide 17: Select the COM port COM 1, Baud rate 19200 ,Data bits 8 Parity Even, Stop Bits 1, Flow Control None then click Next
These will be the Modbus network COM settings you chose, do not confuse them with the boot loader settings

## Slide 18: The default below works ok, click Next

## Slide 19: Click Next and review the setting Click Finish

## Slide 20: Add the first slave device, (meter) Click on ,Click to add a device

## Slide 21: Type in a Device name, click Next

## Slide 22: Select the Device ID (node address), click Next

## Slide 23: These defaults values work, click Next

## Slide 24: These defaults are ok, click Next

## Slide 25: These defaults are ok, click Next

## Slide 26: These defaults are ok, click Next

## Slide 27: These defaults are ok, click Next

## Slide 28: These defaults are ok, click Next

## Slide 29: These defaults are ok, click Next

## Slide 30: These defaults are ok, click Next

## Slide 31: You can review all of the new device setting you have done here, once your satisfied click Finished

## Slide 32: You have configured the Master and the 1st slave.
You will need to configure the Tags that will contain the data from your meter for an OPC client to see the data values.
You will need the register list for the meter you are using to look up the register number, the data type used, and the byte order

## Slide 33: To make a new Tag click on either add Tag icon

## Slide 34: When Add Tag is clicked the dialog box below will appear From the information on the meter Holding Register list fill in: Tag Name, Register Address, Description, Data type, read/write

## Slide 35: KEPserverEX data type name descriptions

## Slide 36: The last tag was a Float data type, this time I will add a 32 bit unsigned integer (“DWord” in KEPserverEx). The Totalizer is at address 40003 to 40004.

## Slide 37: This time I’ll add an ASCII String data type. From the Register list I see that the flow units are on registers 40011 to 40013, using data type “string”.
When using a string, KEPserverEx needs to know how many characters are in the string, and what order the characters appear.
The .4 indicates 4 characters and H indicates the order of the characters (HiLo).

## Slide 38: Now start the Kepserver’s built-in Quick OPC client by clicking the Hammer icon.
Notice Kepserver added a zero to the register addresses. This is done for compatibility with older Modbus devices.

## Slide 39: The Quick Client will start and show all the tags. Including the ones I just made and the automatically generated System tags.

## Slide 40: Click on the Modbus Master.620_1 folder to see the Tags I made for Flow, Total, and Units
The Flow Rate, Flow Units, and Totalizer values are in the Value column

## Slide 41: Kepserver summary
At this point you should be able to:
  Use the Sierra Boot loader to change a meter’s com settings
  Add a new Modbus-RTU master to Kepserver
  Add a new Modbus-RTU slave device
  Add device Tags to read values from the slave device
  Start the Kepserver Quick Client to read values from a slave device
  Other Modbus equipped Sierra devices will use the same setup, only different register lists will be used.

## Slide 42: END of Kepserver Power Point presentation